## Overview
Technology category |  | Coal |  | Summary
Version |  |  | 1.3 | The generating costs of both PWD as IGCC have increased. The main line of reasoning found is that costs have increased steadily over the last years due to the combination of increased in demand of these technologies and an increase of commodities (steel) and energy (see notes EIA and Energieraad). Unfortunatly the literature study has limited value as reports are very general or do not include the detailed information needed to come to these conclusions (e.g. reasons cost escalations), therefore an external expert has to be consulted.
Author |  | NR
Date | Version | Changes
2011-12-07 | 1 | First version
2012-01-04 | 1.1 | added ETM cost calculations
2012-01-16 | 1.2 | new table format
2012-02-21 | 1.3 | Added fuel and co2 calculations
|  |  |  | Total generation costs calculation outcomes: Coal PWD |  | New ETM | Old ETM | %∆
Coding |  |  |  | Total electricity generation costs | EURO/MWh | 45.4585 | 43.8166 | 3.747%
Example | Value extracted from one of the reports referred to in notes |  |  | Total capital costs | EURO/MWh | 11.7333 | 10.042 | 16.84%
Example | Calculation |  |  | Total depreciation costs | EURO/MWh | 5.3946 | 5.9952 | -10.02%
Example | (default) Value as set by the ETM on 23-11-2011 |  |  | Total operating costs | EURO/MWh | 4.6233 | 4.0721 | 13.54%
|  |  |  | Fixed operating costs | EURO/MWh | 2.8777 | 1.1049 | 160.4%
Introducing remarks |  |  |  | Variable operating costs | EURO/MWh | 1.7456 | 2.9672 | -41.17%
· In this file you can find the research done on the generating costs of coal. |  |  |  | Total CO2 costs | EURO/MWh | 0.85301 | 0.85301 | 0%
· This research will update the attributes of this technology (see output tab) which will be used for the ETM. |  |  |  | Total fuel costs | EURO/MWh | 22.8543 | 22.8543 | 0%
· Made fully available and transparent with the goal to stimulate the debate which will hopefully lead to a
continuous improvement of the ETM. |  |  |  | Total generation costs calculation outcomes: Coal IGCC |  | New ETM | Old ETM | %∆
· This research has made possible with help of the consulted sources, the knowledge within Quintel Intelligence |  |  |  | Total electricity generation costs | EURO/MWh | 55.8391 | 56.1813 | -0.6091%
and external validation |  |  |  | Total capital costs | EURO/MWh | 17.7847 | 15.2195 | 16.85%
· The following excel tabs relay information in the following order: |  |  |  | Total depreciation costs | EURO/MWh | 10.1627 | 8.6969 | 16.85%
Sources à Notes à Calculations à Output |  |  |  | Total operating costs | EURO/MWh | 4.1845 | 8.2044 | -49%
· Supporting information is provided in the tabs: assumptions, supporting variables, reading guide |  |  |  | Fixed operating costs | EURO/MWh | 3.1625 | 3.3575 | -5.808%
· For more information about the ETM and its cost calculations visit |  |  |  | Variable operating costs | EURO/MWh | 1.022 | 4.8469 | -78.91%
http://wiki.quintel.com/index.php/Documentation |  |  |  | Total CO2 costs | EURO/MWh | 0.85301 | 0.85301 | 0%
|  |  |  | Total fuel costs | EURO/MWh | 22.8543 | 23.2074 | 0%

## Assumptions
List of most important assumptions used
Assumptions
All costs are in 2010 EURO excl tax and subsidies
In calculations when certain values were not found values as set by the ETM on 23-11-2011 were used as an assumption (these values are colored red).
Powerplant is constucted on undeveloped (e.g. greenfield) land.

## Sources
List of sources used for converter specifications
| Number | source | used in calculations? | Refman ID | Technology | Sources used before (2008)
| 1 | Arcadis_17082009_Milieueffectrapport aardgasgestookte elektriciteitscentrale eemshaven | No, lack data |  | Coal pwd | Confidential
| 2 | Broek_20100723_Modelling approaches to assess and design CO2 capture, transport and storage | Yes | 2010_UU_CS |  | IEA_200810_CO2 capture and storage.pdf
| 3 | CE Delft_201110_Aardgas en biomassa als brandstof voor RWE Eemshaven kolencentrale | Yes | 2011_CE_BE_3 |  | CE_2006_welke nieuwe E-centrale_Vernieuwd CE model.pdf
| 4 | CEC_200907_Comparative costs of California central station electricity generation technologies | No, US data
| 5 | DEA_20100601_Technology Data for Energy Plants | No, lack data |  | Coal pwd CCS | Confidential
| 6 | DECC_20110501_Costs of low-carbon generation technologies | No, new data available |  |  | Clingendael_200809_CCS - A reality check for the Netherlands.pdf
| 7 | DECC_201108_Electricity Generation Cost Model 2011 update_revison 1 | No, UK data. |  |  | McKinsey_200810_CCS - Assessing the Economics.pdf
| 8 | ECF_2011_Power Perspectives 2030 | No, scenario 2020 case |  |  | IEA_200810_CO2 capture and storage.pdf
| 9 | ECN_201003_Kernenergie en Brandstofmix | No, ECN makes use of the IEA_NEA_2010 figures |  |  | CE_2006_welke nieuwe E-centrale_Vernieuwd CE model.pdf
| 10 | ECN_201012_Kolencentrales Eemshaven - dwingende redenen openbaar belang | No, lack data |  | Coal conventional | IEA_2007_Fossil fuel fired power generation.pdf
| 11 | Ecofys_200611_Kernenergie of Kolenvergassing | No, too old |  |  | NEA_IEA_2000503_Projected Costs of Generating Electricity 2005 update.pdf
| 12 | EIA 201011_Updated capital costs estimates for electricity generation plants | No, US data
| 13 | Energieraad_20080902_Waterstof uit kolen | No, but informative
| 14 | GCI_08032011_economic-assessment-carbon-capture-and-storage-technologies-2011-update | No, Australian data
| 15 | Harvard_20100521_Roadmap 2050 - A practical guide to a prosperous, low-carbon Europe | Yes | 2010_HVD_EaGN | Coal lignite | IEA_2007_Fossil fuel fired power generation.pdf
| 16 | http://www.energiegids.nl/nieuws/details.tiles?doc=/content/energie/nieuws/2010/03/19/OE-Shell-Essent.xml | No, but informative
| 17 | IEA and NEA_2010_Projected costs of generating electricity | Yes | 2010_IEA_EM.ec
| 18 | IEA_2010_Cost and performance of carbon dioxide capture from power generation | No, lack data
| 19 | KEMA_200809_Startnotitie 400-450MWe | No, too old |  | Coal oxyfuel CCS | Estimate
[5 empty] | Coal IGCC | Confidential
IEA_200810_CO2 capture and storage.pdf
CE_2006_welke nieuwe E-centrale_Vernieuwd CE model.pdf
[5 empty] | Coal IGCC CCS | Confidential
Clingendael_200809_CCS - A reality check for the Netherlands.pdf
McKinsey_200810_CCS - Assessing the Economics.pdf
IEA_200810_CO2 capture and storage.pdf
CE_2006_welke nieuwe E-centrale_Vernieuwd CE model.pdf
[5 empty] | Co-firing Coal | Confidential

## Notes
Source | Page | Notes | Calculations etc | Unit
DECC_201108_Electricity Generation Cost Model 2011 update_revison 1 | 81 |  |  |  | NOAK
|  |  | 5 | yr | Construction period
|  |  | 30 | yr | Plant operating period
|  |  | 41% | % | Efficiency
|  |  | 51750 | £/MW/yr | O&M fixed fee
|  |  | 3000 | £/MW/yr | Insurance
|  |  | 1 | £/MWh | O&M variable fee
|  |  | 1 | % | average load factor
|  |  | 1.4 | £/kW | Infrastructure costs
|  |  | 2300 | £/kW | EPC costs
|  |  | 2.2% | % | Average degredation
|  |  | 5050 | £/MW | Connection and UoS charges
|  |  | 870 | MW | Capacity
23
FOAK
|  |  | 5 | yr | Construction period
|  |  | 20 | yr | Plant operating period
|  |  | 37.3% | % | Efficiency
|  |  | 81000 | £/MW/yr | O&M fixed fee
|  |  | 4950 | £/MW/yr | Insurance
|  |  | 2.9 | £/MWh | O&M variable fee
|  |  | Not reliable | % | average load factor
|  |  | 44 | £/kW | Infrastructure costs
|  |  | 4844 | £/kW | EPC costs
|  |  | 2.4% | % | Average degredation
|  |  | 7.8 | £/MWh | CO2 transport and storage costs
ASC PC
NOAK
| 20 |  | 3 | yr | Construction period
|  |  | 35 | yr | Plant operating period
|  |  | 46% | % | Efficiency
|  |  | 35000 | £/MW/yr | O&M fixed fee
|  |  | 2500 | £/MW/yr | Insurance
|  |  | 1 | £/MWh | O&M variable fee
|  |  | Not reliable for UK | % | average load factor
|  |  | 22.5 | £/kW | Infrastructure costs
|  |  | 1600 | £/kW | EPC costs
|  |  | 2.9% | % | Average degredation
|  |  | 1600 | MW | capacity
|  |  | 0.44 | % | efficiency
fuel cost
| 21 | Coal ASC PC CCS
FOAK
|  |  | 5 | yr | Construction period
|  |  | 20 | yr | Technical lifetime
|  |  | 36.7% | % | Efficiency
|  |  | 71520 | £/MW/yr | O&M fixed fee
|  |  | 4000 | £/MW/yr | Insurance
|  |  | 2.1 | £/MWh | O&M variable fee
|  |  | Not reliable for UK | % | average load factor
|  |  | 27.5 | £/kW | Infrastructure costs
|  |  | 3530 | £/kW | EPC costs
|  |  | 2.4% | % | Average degredation
|  |  | 7.8 | £/MWh | CO2 transport and storage costs
IEA and NEA_2010_Projected costs of generating electricity
PWD
| 60 |  | 2171 | USD/kWe | Overnight costs
|  |  | 2756 | USD/kWe | Investment costs
|  |  | 585 | USD/kWe | IDC
|  |  | 3.97 | USD/MWh | Operating and Maintanance costs
|  |  | 780 | MW | Capacity Gross
|  |  | 0.46 | % | Efficiency
|  |  | 28.75 | USD/MWh | Fuel cost
| 37 | The load factor is fixed either by the general assumption of 85%
|  | (for nuclear, coal, and gas) or by national assumptions (for renewables). | 85% | % | Load factor
90
| 4 | IGCC is very different from conventional coal-fired plants, having more similarities to natural
gas combined cycle gas turbine (CCGT) plants. Fuel gas is produced from coal in a gasifier, cleaned
and then fed to a gas turbine with heat recovery to generate steam to drive the turbines. Gasification
takes place in a pressurised vessel with partial combustion of the coal in a limited supply of air
or oxygen, with or without steam. Low emissions are achieved as an inherent part of the process
and the potential for high efficiency is comparable to that for supercritical PC plants. However,
complexity and cost mean that IGCC has not yet achieved commercialisation, although a small
number of demonstration plants are operating successfully at the 250 MWe to 300 MWe scale.
The largest plant currently operating, Puertollano IGCC, is 335 MWe (gross), around 300 MWe net.
DECC_20110501_Costs of low-carbon generation technologies
6_5
|  |  | 39% | % (LHV) | efficiency ASC PC CCS
|  |  | 44% | % (LHV) | efficiency ASC PC Oxy CCS
|  |  | 37% | % (LHV) | efficiency ASC PC IGCC CSS
|  |  | 40 | y | Plant life ASC PC CCS
|  |  | 40 | y | Plant life ASC PC Oxy CCS
|  |  | 30 | y | Plant life ASC PC IGCC CSS
| 3_70 | PC CCS
|  |  | 1121 | £/kW | Specific investment - CO2 capture
|  |  | 1600 | £/kW | Base power plant
CEC_2009_Comparative costs of California central station electricity generation technologies
Coal IGCC
|  |  | 3184 | USD/kW | Instant cost
|  |  | 52.35 | USD/kW/y | Fixed O&M
| 46 |  | 9.57 | USD/MWh/y | Variable O&M
IEA_2010_Cost and performance of carbon dioxide capture from power generation
22
Coal PC CCS
22
|  |  | 85% | % | Capacity factor
|  |  | 4 | y | Construction time
|  |  | 40 | y | lifetime
33
Coal PC CCS and 'regular' USC PC
Coal Oxy CCS
|  |  | 3419 | USD/kW | Overnight cost
|  |  | 35% | % | Efficiency
| 38 | Coal IGCC (and CCS)
IGCC
|  |  | 2586 | USD/kW | Overnight cost
|  |  | 0.331 | % | Efficiency
|  |  |  | MW | Capacity
IGCC CCS
|  |  | 3714 | USD/kW | Overnight cost
PC USC CCS
PC USC CCS
|  |  | 3166 | USD/kW | Overnight cost
|  |  | 35% | % | Efficiency
|  |  | 1176 | USD/kW | Costs of CO2 capture
|  |  | 1990 | USD/kW | Investment plant
PC USC
|  |  | 1990 | USD/kW | Overnight cost
|  |  | 44.9% | % | Efficiency
|  |  | 689 | MW | Capacity
Arcadis_17082009_Milieueffectrapport aardgasgestookte elektriciteitscentrale eemshaven
GCI_08032011_economic-assessment-carbon-capture-and-storage-technologies-2011-update
IGCC
49
18
|  |  | 1919 | USD/kW | Overnight costs
|  |  | 19378000 | USD | Fixed O&M
|  |  | 33410.3448 | USD/MW | Fixed O&M
|  |  | 4.82 | USD/MWh | Variable O&M
DEA_20100601_Technology Data for Energy Plants | 15
|  |  | 1450000 | EUR/M | Investment costs
EIA 201011_Updated capital costs estimates for electricity generation plants | 156
APC
|  |  | 35.97 | USD/kW | Fixed costs
|  |  | 4.25 | USD/MWh | Variable costs
|  |  | 3167 | USD/kW | Overnight costs
|  |  | 650 | MW | Capacity
|  |  | 38.78% | % | Efficiency
APC CCS
|  |  | 76.62 | USD/kW | Fixed costs
|  |  | 9.05 | USD/MWh | Variable costs
|  |  | 5099 | USD/kW | Overnight costs
IGCC
|  |  | 59.23 | USD/kW | Fixed costs
|  |  | 6.87 | USD/MWh | Variable costs
|  |  | 3565 | USD/kW | Overnight costs
|  |  | 600 | MW | Capacity
|  |  | 39.22% | % | Efficiency
IGCC CCS
|  |  | 69.3 | USD/kW | Fixed costs
|  |  | 8.04 | USD/MWh | Variable costs
|  |  | 5348 | USD/kW | Overnight costs
3_3
Broek_2010_Modelling approaches to assess and design CO2 capture, transport and storage | 236
PC
|  |  | 77 | EURO/kW | Fixed cost
|  |  | 0.36 | EURO/GJ | variable cost
|  |  | 1598 | EURO/kW | Investment cost
|  |  | 0.46 | % | Efficiency
IGCC
|  |  | 71 | EURO/kW | Fixed cost
|  |  | 0.29 | EURO/GJ | variable cost
|  |  | 2005 | EURO/kW | Investment cost
|  |  | 0.46 | % | Efficiency
61
32
101
104
129
Coal
|  | A life time of 30 years is chosen for coal‐fired and gas‐fired power plants, 20 years for wind turbines, 20 years for PV, and 40 years for nuclear power plants in the normal vintage variants. In the EV variants we prolong the life times to 40 years for gas‐fired, 50 years for coal‐fired, and 60 years for nuclear power plants. | 30 | y | Lifetime
CE Delft_201110_Aardgas en biomassa als brandstof voor RWE Eemshaven kolencentrale
|  |  | 1580 | MW | Capacity
|  |  | 0.47 | % | Efficiency
|  |  | 12 | EURO/MWh | Fixed costs
|  |  | 2 | EURO/MWh | Operating costs
|  |  | 1650 | EURO/kW | Investment costs
ECN_201003_Kernenergie en Brandstofmix | 68 | De prijzen van zowel hernieuwbare als conventionele energietechnologieën nemen sinds 2002 vooral toe.38 Dit geldt voor zowel conventionele kolen- en gascentrales, kerncentrales, als tevens voor duurzame technologie zoals windenergie en zon-PV. Deze algehele kostenescalatie werd veroorzaakt door een combinatie van toenemende vraag naar deze technologieën en toenemende kosten voor grondstoffen (staalprijzen) en energie. Waar voor innovatieve en duurzame technologieën eerder vaak leercurves werden verondersteld die - bij verdere toename van het opgesteld vermogen - een kostendaling zouden moeten laten zien, blijkt dat concept in de afgelopen jaren niet dominant te zijn geweest in de kostenontwikkeling. De OECD (OECD, 2010) stelt dat in de periode 2004-2008 een kostenstijging van minimaal 50% is waargenomen. Een studie van Jacobs (Jacobs, 2008) bevestigt die ontwikkeling.
KEMA_200809_Startnotitie 400-450MWe | 11 | Het doel van C.GEN is om een waterstofelektriciteitscentrale te bouwen. Deze combinatie van een vergassingsinstallatie en een elektriciteitscentrale heeft een bruto elektrisch vermogen van 400-450 MWe en voorziet in CO2 afvang.
| 15 | Het technisch concept
Het principe van vergassing is een verbranding met een ondermaat aan zuurstof. Hierbij kan
het verbrandingsproces zichzelf in stand houden en ontstaat een brandbaar gas (syngas) dat
na schoonmaak benut kan worden voor verbranding. Het syngas bestaat voornamelijk uit
koolstofmonoxide (CO) en waterstof (H2). Een shiftreactor zorgt voor de omzetting van de
CO met water in H2 en CO2, waarna CO2 wordt afgevangen.
Voorafgaande aan de vergassing worden de vaste brandstoffen gemalen en gedroogd. In de
vergasser reageert het ruwe materiaal met stoom en/of zuurstof onder een hoge temperatuur
(circa 1500 °C) en druk. De zuurstofproductie zal hoogstwaarschijnlijk worden verzorgd door
een luchtscheidingsinstallatie die werkt volgens het cryogene procédé van luchtscheiding
door gefractioneerde destillatie. Alvorens het door de vergasser gevormde syngas verbrand
kan worden in de gasturbine, dient het gas ontdaan te worden van verschillende
verontreinigingen en van de CO2. De warmte die beschikbaar komt bij de noodzakelijke
afkoeling van het syngas kan benut worden om stoom op meerdere drukniveau’s te
genereren.
Het gereinigde gas wordt door middel van gasturbines en stoomturbines omgezet in
elektriciteit en warmte (zie figuur 4.1 voor een schematisch overzicht). Het rendement van de
centrale is afhankelijk van de exacte uitvoeringsvorm. C.GEN heeft nog geen beslissing
genomen over de exacte uitvoeringsvorm van het vergasserdeel van de centrale.
De vergassingstechniek biedt C.GEN een grote flexibiliteit ten aanzien van brandstofkeuze.
Dit biedt de mogelijkheid voor C.GEN om afhankelijk van milieueisen, brandstofprijzen en
andere factoren een ideale mix samen te stellen van steenkolen, petcokes, aardgas en
biomassa. Een ander voordeel van de vergassingstechnologie vormen de lagere emissies in
vergelijking met klassieke poederkool-centrales en de energetisch veel gunstiger CO2-
afvang.
| 16 | Figuur 4.1 Schematisch overzicht van de kolenvergassingscentrale (indicatief)
| 17 | STEG gedeelte
De centrale zal worden uitgevoerd als STEG (SToom- En Gasturbine). Dit betekent dat de installatie zal worden opgebouwd uit een gasturbine, verbonden met een afgassenketel en een stoomturbine. Voor NOx verwijdering uit de rookgassen wordt een SCR geïnstalleerd.
De gasturbine bestaat uit een compressor, één of meer verbrandingssecties en tenslotte de
turbine zelf, die de generator aandrijft. De uitlaatgassen stromen naar de afgassenketel
waarin stoom wordt gegenereerd. De stoom drijft de verschillende trappen van de
stoomturbine aan. Met de generator wordt de mechanische energie van de turbines omgezet
in elektriciteit. De geëxpandeerde stoom wordt in een condensor gecondenseerd door
koeling met oppervlaktewater.
Het is mogelijk dat de afgassenketel voorzien worden van bijstookbranders om meer
flexibiliteit in stoomlevering te bereiken of extra elektrisch piekvermogen beschikbaar te
krijgen.
Om het ontstaan van stikstofoxiden tegen te gaan wordt het waterstofgas "verdund" met
stikstof of stoom. Het effect daarvan is dat te hoge vlamtemperaturen en daarmee te hoge
emissies van stikstofoxiden worden voorkomen. Bovendien zullen in de gasturbines speciale
branders worden gemonteerd die de vorming van stikstofoxiden reduceren en zal de
afgasketel na de gasturbine worden uitgerust met een SCR.
Gasstromen die onder incidentele omstandigheden niet in de gasturbines kunnen worden
verbrand, worden in een fakkel verbrand. Dit doet zich met name voor bij het opstarten en uit
bedrijf gaan van de vergasser alsmede bij noodstops.
Ecofys_200611_Kernenergie of Kolenvergassing | 6 | O&M en brandstofkosten KV-STEG
Kosten voor O&M bij een KV-STEG bedragen ca. 0,8 tot 1,5 €ct/kWh (ECN, 2005a en Hendriks et al., 2004). Brandstofkosten voor KV-STEG met CO2-afvang zijn ca. 1,6 ct€/kWh bij een kolenprijs van 45 €/ton (ECN, 2005a). De kolenprijs bedraagt op dit moment 60 €/ton. Voor elektriciteitsopwekking met fossiele brandstoffen geldt een sterke gevoeligheid van kosten elektriciteitsopwekking voor een stijging van brandstofprijzen. Een verdubbeling van de kolenprijs betekent voor een KV-STEG met CO2-afvang dat kosten voor elektriciteitsopwekking toenemen met ca. 25%
| 6 | Kapitaallasten
De investeringskosten voor een KV-STEG zijn ca. 1600 €/kW en met CO2-afvang ca. 2000 €/kW. Kapitaallasten voor een KVSTEG met CO2-afvang komen dan uit op ca. 2,8 €ct/kWh (ECN, 2005a). Ter vergelijking, de investeringskosten voor een poederkoolcentrale zijn ca. 1200 €/kW en met CO2-afvang 1800 €/kW. Kapitaallasten voor een STEG zijn ca. 560 €/kW en met CO2-afvang ca. 950 €/kW. (Hendriks et al., 2004)
De kapitaallasten van een kerncentrale en een KV-STEG met CO2-afvang zijn redelijk vergelijkbaar. De relatief hoge kapitaalslasten voor beide opties is een nadeel, zeker in een liberale markt waarin een hogere investering meer risico betekent
http://www.nuon.com/nl/pers/persberichten/20110407/Nuon-stelt-vergassingstechnologie-in-nieuwe-centrale-uit.jsp |  | Nuon stelt vergassingstechnologie in nieuwe centrale uit
Nuon heeft besloten de plannen voor mogelijke vergassing van biomassa en kolen in haar nieuwe elektriciteitscentrale in de Eemshaven uit te stellen. De bouw van de gasgestookte centrale Nuon Magnum verloopt voorspoedig. Deze centrale is eind 2012 gereed en levert elektriciteit aan 2 miljoen huishoudens.
Energieraad_20080902_Waterstof uit kolen |  | Vergassingstechnologie. Bij kolenvergassing worden de kolen tezamen met zuurstof, onder hoge temperatuur en druk, vergast tot een mengsel van koolmonoxide en waterstof. Dit mengsel van CO en H2, ook wel ‘syngas’ of synthesegas genoemd, is de basis van een scala aan chemische processen maar kan ook rechtstreeks als brandstof dienen. Vooraf aan verdere verwerking wordt het ‘syngas’ gekoeld met water dat als stoom in een turbine stroom kan opwekken. Het is eenvoudiger om het synthesegas te reinigen, dan de afgassen die bij klassieke (poeder-) kolenverbranding vrijkomen. Dit maakt niet alleen afvang van CO2 goedkoper, maar ook de afvang van schadelijke stoffen als SO2, NOx en metalen. Het syngas kan vervolgens in de ‘shift-reactor’, onder toevoeging van stoom, worden omgezet in (onzuivere) waterstof en CO2. Dit gebeurt overigens in twee stappen, maar is in de figuur als een enkel blok weergegeven. De waterstof kan verder verwerkt worden, of rechtstreeks verbrand. De CO2 wordt er met een fysisch of chemisch proces uit de gasstroom gewassen en in geconcentreerde vorm afgevoerd om opgeslagen te worden. Kolenvergassing is een technologie die ontwikkeld is in Duitsland (ten tijde van de Tweede Wereldoorlog) en door Shell in Amsterdam sinds de jaren ‘70. De Shell-technologie is op commerciële schaal toegepast in de centrale van Buggenum (momenteel eigendom van NUON), waar ook het bijstoken van biomassa (tot 30%) is aangetoond. Deze technologie is vooraanstaand in de wereld en hiermee zijn een aantal fabrieken gerealiseerd onder andere in China. Daar wordt de technologie ook gebruikt voor de productie van waterstof, van methanol en voor de vervaardiging van ammoniak (kunstmest). Daarnaast is in Nederland ervaring opgedaan met vergassing in een installatie in Geertruidenberg. Geen van de bestaande installaties is echter uitgerust met CO2-afvang en -opslag. Belangrijke reden om een grootschalige demonstratiefabriek inclusief opvang en opslag te bouwen is de gecombineerde technologie te demonstreren en hiermee ervaring op te doen. Daarnaast kan worden aangetoond dat een gecombineerde installatie die continu in bedrijf kan zijn de bedrijfszekerheid biedt die in de energievoorziening vereist is. Ook bij ECN wordt onderzoek gedaan aan vergassingstechnologie, met name voor de vergassing van biomassa. Op termijn is ook dat een flexibele optie voor het produceren van gas.
Kosten Bij het beoordelen van de kosten van een geavanceerde kolenvergasser is het vooral belangrijk om de relatieve kosten ten opzichte van het alternatief elektriciteitsopwekking via directe verbranding van kolen in te schatten om te kunnen beoordelen of marktpartijen geïnteresseerd kunnen worden. Dat staat los van de maatschappelijke kosten-baten van de twee hier aan de orde zijnde kolenopties die marktpartijen niet gemakkelijk kunnen meenemen in hun investeringsbeslissing. Dit geldt met name voor de vergrote flexibiliteit en diversificatie van brandstoffen. Een typische vergassereenheid met bijbehorende randapparatuur kan ongeveer 2000 ton kolen per dag verwerken. Hoewel de kosten van de vergasser zelf goed zijn in te schatten, geldt dat minder voor de apparatuur eromheen (voor de gasbehandeling bijvoorbeeld). Door verschillende partijen zijn kostenberekeningen en vergelijkingen gemaakt. Bij gelijke kosten voor de kolen wordt de nauwkeurigheid van deze schattingen met name beïnvloed door de geschatte investeringskosten welke de laatste tijd zeer sterk zijn gestegen door de grote stijging van de kosten van apparatuur, leidingwerk, staal et cetera. De Raad heeft daarom recente updates laten maken van de vergelijkende schattingen, maar claimt geen grote nauwkeurigheid. De conclusie is dat bij vollast de kosten van geproduceerde elektriciteit, bij gelijke prijzen voor kolen en CO2 ,voor kolenvergassing met CCS iets lager zijn dan voor een conventionele kolencentrale met CCS. We kunnen ervan uit gaan dat de kosten voor beide technologieën ongeveer dezelfde zijn. Wanneer de vraag/aanbod situatie echter zodanig is dat de elektriciteitsproductie door de centrale moet worden gereduceerd en deze bijvoorbeeld op middenlast moet gaan draaien, wordt het kostenplaatje voor kolenvergassing aanzienlijk beter dan voor de conventionele kolencentrale. Dit omdat de vergassingscentrale dan op vollast kan blijven draaien en het gasoverschot aan het gasysteem kan leveren. Het is met name deze flexibiliteit waardoor kolenvergassing aantrekkelijk wordt.
http://www.energiegids.nl/nieuws/details.tiles?doc=/content/energie/nieuws/2010/03/19/OE-Shell-Essent.xml |  | Geplande kolenvergasser Shell en Essent financieel onhaalbaar
Het plan van Shell en Essent om een kolenvergassingscentrale te bouwen is van de baan. Het is commercieel niet haalbaar, zo laat Essent desgevraagd weten. De centrale van 1000 MWe was gepland in Zuid-West Nederland. Er is sinds de aankondiging in december 2008 gekeken naar een combinatie van een hoogrendement vergassingsfabriek, stroomopwekking en afvang en opslag van CO2 (CCS). Door vergassing van steenkool en vaste biomassa ontstaat synthesegas waaruit waterstof wordt gemaakt die vervolgens via turbines in elektriciteit wordt omgezet. Om de centrale met CCS financieel haalbaar te maken is overheidssteun nodig. Tegenover milieu-organisatie Greenpeace heeft Shell verklaard dat overheidssteun voor de CO2-opslag onwaarschijnlijk is, nu Nuon in de Eemshaven eenzelfde soort centrale bouwt en daarmee op de dezelfde Europese subsidiepot mikt. Het nieuwe moederbedrijf van Essent, RWE, was inmiddels al begonnen met de bouw van de kolengestookte Eemscentrale. Deze centreale wordt een kolencentrale waar biomassa wordt meegestookt. De centrale krijgt een hoger rendement (46%) dan de huidige typen kolencentrales (circa 30%). “Daarnaast zijn we druk bezig om maximaal in te zetten op CCS. Daarbij kijken we naar lege gasvelden onshore en niet offshore. Bij de geplande centrale met Shell keken we wel naar opslag in zeebodem”, aldus Essent-woordvoerder Jeroen Brouwers. Dat betekent dat voor de CO2-opslag van de in aanbouw zijnde Eemscentrale met omwonenden van de te vullen gasvelden veel gecommuniceerd gaat worden. Maar of daarbij ook gedacht wordt aan mogelijke compensatieregelingen, wilde Brouwers niets over kwijt.
ECF_2011_Power Perspectives 2030 | 75
Harvard_20100521_Roadmap 2050 - A practical guide to a prosperous, low-carbon Europe
| 2 |  |  |  | Coal
|  |  | 1500000 | EURO / MW | Capex
|  |  | 20000 | EURO / MW | OPEX fix
|  |  | 1 | EURO / MWh | OPEX variable
|  |  | 4 | year | Construction time
|  |  | 40 | year | Lifetime
|  |  | 0.07 | % | WACC
30
31
32
| 33 | Basic assumptions: WACC (real, after tax): 7%
Note on E7: Nick Rothengatter: Assumed that fixed maintenance price is £46000/MW + £5million a year for staff costs.
Note on E9: Nick Rothengatter: Assumed to be a similar cost to that for coal technology as there is a comparable amount (and cost) for consumables. Water treatment (and therefore costs) assumed to be 3 times the amount of CCGT (i.e. from the amount of steam used).
Note on G11: Nick Rothengatter: Includes construction of HV spur and substation at tee point, gas and CO2 pipelines (to national transmission system) and rail spurs where appropriate.
Note on E14: Nick Rothengatter: Based on NG UoS charge zones. Zones in which generation could be built were selected, then max, average and min selected as high, med and low levels.
Note on E52: Nick Rothengatter: Figure is based on value used for IGCC + £15750/MW for CCS technology. FOAK prices assumed to be 20% higher than NOAK
Note on E54: Nick Rothengatter: Additional CCS cost is assumed as £1.40/MWh, which is also based on various studies and expert opinion. This is relatively comparable to the CAPEX increments for CCS technology. Additional allowance made for water treatment - assumed to be three times the amount of CCGT (on the same basis of coal assumption) FOAK prices assumed to be 20% higher than NOAK
Note on G56: Nick Rothengatter: Includes construction of HV spur and substation at tee point, gas and CO2 pipelines (to national transmission system) and rail spurs where appropriate.
Note on E92: Nick Rothengatter: Coal technology is very well established in the power industry and the duration of project periods tends not to be suspectible to major fluctuations. These figures are based on many years of involvement with coal technology projects. source: DECC_201108_Electricity cost model 2011 update (revision 1) P.39
Note on E95: Nick Rothengatter: Assumed that fixed maintenance price is £32000/MW + £5million a year for staff costs. source: DECC_201108_electricity cost model update (revision 1) P. 39
Note on G95: Nick Rothengatter: The fixed operating costs are considerably more than for CCGTs as boiler plant, fuel and ash handling and FGD all require more hands-on operation than largely automated gas fired plant. P.28 Mott MacDonald
Note on E97: Nick Rothengatter: Variable cost made up of a cost for FGD consumable (i.e. limestone) and cost for water treatment. Water treatment (and therefore costs) assumed to be 3 times the amount of CCGT (i.e. from the amount of steam used). FGD costs assume £30/tonne for limestone. Other assumptions are 2% coal sulphur content, +/- 25% (high & low figures). Therefore between £6m and £10m for limestone. 85% then taken for allowance of running time per year. Source: DECC_201108_Electricity cost model 2011 update (revision 1) P.39
Note on G99: Nick Rothengatter: Includes construction of HV spur and substation at tee point, gas and CO2 pipelines (to national transmission system) and rail spurs where appropriate..
Note on E100: Nick Rothengatter: As mentioned above, large super critical coal units have seen among the most rampant cost escalation due to bottlenecks in supply of specialist forgings, high pressure pipes and thick rolled flat plate. P. 28 The short term outlook for prices of advanced coal plant is almost certainly one of declining dollar prices as the overheated market of 2008 cools. The decline is unlikely to be as anything like as marked as the ascent given that it will take some time (3-4 years) to invest in facilities to de-bottleneck the supply chain. P.30
Note on E101: Nick Rothengatter: PB notes that some of the calculated figures, notably the average degradation and average availability, are not representative of expected performance during the expected operational life of the plant. For example, the average availability figure does not account for the actual operational life of the plant which is being modelled. --> therefore used old Mott MacDonald figure
Note on E141: Nick Rothengatter: Assumed that fixed maintenance price is £56500/MW + £5million a year for staff costs. FOAK prices assumed to be 20% higher than NOAK
Note on E143: Nick Rothengatter: Based on variable O&M cost for coal (without CCS), plus an additional variable cost for CCS technology. Additional CCS variable O&M costs is taken as £1.12/MWh, which is based on various studies and confirmed by CCS experts. FOAK prices assumed to be 20% higher than NOAK
Note on G145: Nick Rothengatter: IIncludes construction of HV spur and substation at tee point, gas and CO2 pipelines (to national transmission system) and rail spurs where appropriate.
Note on E185: Nick Rothengatter: both variable and fixed
Note on G382: Nick Rothengatter: Instant cost, sometimes referred to as overnight cost P.2
Note on E558: Nick Rothengatter: 46% IGCC! Welke is dat!
Note on G696: Nick Rothengatter: what is emant by materials?

## Calculations
Checks and balances and other calculations
|  |  |  | Coal PWD | [8 empty] | Coal IGCC
Sources
|  |  | Data | New ETM | Old ETM | %∆ | %SD | IEA | IEA_NEA | Broek | Harvard | Comments | New ETM | Old ETM | %∆ | %SD | IEA | Broek | Harvard | Comments
Units/Region
Technical specifications
Capacity/yield
|  | Production capacity Gross | MWe | 800 | 800 | 0% |  | 695.9596 | 780 | 800 | 800 | Assumed to be 800 MW, as standard in the ETM | 800 | 800 | 0% |  | 800 | 800 | 800 | Assumed to be 800 MW, as standard in the ETM
|  | Average effective output of nomimal capacity over lifetime | % | 99% | 99% | 0% |  | 99% | 99% | 99% | 99% | Assumed to be 99%, as standard in the ETM | 98% | 98% | 0% |  | 0.98 | 98% | 99% | Assumed to be 98%, as standard in the ETM
|  | Production capacity Effective | MWe | 792 | 792 | 0% |  | 689 | 772.2 | 792 | 792 | Assumed to be 792 MW, as standard in the ETM | 784 | 784 | 0% |  | 784 | 784 | 792 | Assumed to be 784 MW, as standard in the ETM
|  | Net Electrical yield / efficiency | % | 46% | 46% | 0% |  | 44.9% | 46% | 46% | 46% | Assumed to be 46%, as standard in the ETM | 46% | 45.3% | 1.545% |  | 33.1% | 46% | 45.3% | Set at 46% as indicated by Broek
|  | Capacity factor/ Load factor | % | 79.34% | 79.34% | 0% |  | 79.34% | 85% | 79.34% | 79.34% | Calculation from equivalent full load hours | 72.19% | 72.19% | 0% |  | 72.19% | 72.19% | 72.19% | Calculation from equivalent full load hours
|  | Equivalent full load hours | hours | 6950 | 6950 | 0% |  | 6950 | 7446 | 6950 | 6950 | See comment in this cell for more elaborate argumentation. | 6324.11 | 6324.11 | 0% |  | 6324.11 | 6324.11 | 6324.11 | See comment in this cell for more elaborate argumentation.
|  | Average energy production | GWh/y | 5504.4 | 5504.4 | 0% |  | 4788.55 | 5749.8012 | 5504.4 | 5504.4 | Calculation from equivalent full load hours and effective capacity. |  | 4958.1022 | 0% |  | 4958.1022 | 4958.1022 | 5008.6951 | Calculation from equivalent full load hours and effective capacity.
Other
|  | Construction time | years | 3.5 | 3.5 | 0% |  | 3.5 | 3.5 | 3.5 | 4 | Assumed to be 3,5 ,as standard in the ETM | 5 | 5 | 0% |  | 5 | 5 | 0 | Assumed to be 5 as standard construction time in the ETM
|  | Weighted average cost of capital (WACC) | % | 10% | 10% | 0% |  | 10% | 10% | 10% | 7% | Assumed to be 10%, as standard WACC in ETM for big power plants | 10% | 10% | 0% |  | 10% | 10% | 0% | Assumed to be 10%, as standard WACC in ETM for big power plants
|  | Technical lifetime | years | 40 | 30 | 33.33% |  | 40 | 40 | 30 | 40 | See comment in this cell for more elaborate argumentation. | 30 | 30 | 0% |  | 30 | 30 | 0 | Assumed to be 30, as standard in the ETM
|  | Residual value | EURO/MW | 0 | 0 | 0% |  | 0 | 0 | 0 | 0 | See comment in this cell for more elaborate argumentation. | 0 | 0 | 0% |  | 0 | 0 | 0 | See comment in this cell for more elaborate argumentation.
Finacial specifications
Investment costs
|  | Initial investment costs | EURO/MWe | 1499705.375 | 1250000 | 19.98% | 4.848% | 1424541.5 | 1476280 | 1598000 | 1500000 | Calculated average. | 1928094.05 | 1650000 | 16.85% | 5.641% | 1851188.1 | 2005000 | n/a | Calculated average.
|  | Construction cost | EURO/Mwe | [5 empty] | 1874080
|  | IDC | EURO/Mwe | [5 empty] | 397800
|  | Overnight cost | EURO/Mwe |  |  |  |  | 1424541.5 | 1476280 | [7 empty] | 1851188.1
|  | Contingency costs | EURO/MWe
|  | Bare plant cost (EPC) | EURO/MWe
|  | Owner's costs | EURO/MWe
|  | Decommissioning costs | EURO/MWh | 0 | 0 |  |  |  | 0 | 0 | 0 | See comment in this cell for more elaborate argumentation. | 0 | 0 |  |  | 0 | 0 | 0 | See comment in this cell for more elaborate argumentation.
Operating costs
|  | Fixed operating and maintenance costs | EURO/MWe/year | 20000 | 7679.1513 | 160.4% | 123.6% | 7679.1513 | 0 | 77000 | 20000 | Calculated average. Deviation too big. Expert is consulted, see comment. | 20000 | 21233.2483 | -5.808% | 79.26% | 21233.2483 | 71000 | 20000 | Calculated average. Deviation too big. Expert is consulted, see comment.
|  | Personnel costs | EURO/MWe/year
|  | Insurance costs | EURO/MWe/year
|  | Connection costs | EURO/MWe/year
|  | Other | EURO/MWe/year
|  | Variable operating and maintenance costs | EURO/MWh | 1.7456 | 2.9672 | -41.17% | 59.9% | 2.9672 | 2.9407 | 1.296 | 1 | Calculated average. Deviation too big. Expert is consulted, see comment. | 1.022 | 4.8469 | 0% | 3.044% | 4.8469 | 1.044 | 1 | Calculated average.
|  | Consumables | EURO/MWh
|  | Raw fuel | EURO/MWh
|  | Other | EURO/MWh
Total generation costs calculation outcomes
|  | Total electricity generation costs | EURO/MWh | 45.4585 | 43.8166 | 3.747% |  | 44.0489 | 42.3853 | 56.5844 | 41.29 |  | 55.8391 | 56.1813 | -0.6091% |  | 59.0975 | 65.3934
|  | Total capital costs | EURO/MWh | 11.7333 | 10.042 | 16.84% |  | 11.1452 | 10.7807 | 12.8376 | 8.3094 |  | 17.7847 | 15.2195 | 16.85% |  | 17.0753 | 18.494
|  | Total depreciation costs | EURO/MWh | 5.3946 | 5.9952 | -10.02% |  | 5.1242 | 4.9566 | 7.6643 | 5.3957 |  | 10.1627 | 8.6969 | 16.85% |  | 9.7573 | 10.568
|  | Total operating costs | EURO/MWh | 4.6233 | 4.0721 | 13.54% |  | 4.0721 | 2.9407 | 12.3751 | 3.8777 |  | 4.1845 | 8.2044 | -49% |  | 8.2044 | 12.2709
|  | Fixed operating costs | EURO/MWh | 2.8777 | 1.1049 | 160.4% |  | 1.1049 | 0 | 11.0791 | 2.8777 |  | 3.1625 | 3.3575 | -5.808% |  | 3.3575 | 11.2269
|  | Variable operating costs | EURO/MWh | 1.7456 | 2.9672 | 0% |  | 2.9672 | 2.9407 | 1.296 | 1 |  | 1.022 | 4.8469 | -78.91% |  | 4.8469 | 1.044
|  | Total CO2 costs | EURO/MWh | 0.85301 | 0.85301 | 0% |  | 0.85301 | 0.85301 | 0.85301 | 0.85301 | See comment in this cell for more elaborate argumentation. | 0.85301 | 0.85301 | 0% |  | 0.85301 | 0.85301 |  | See comment in this cell for more elaborate argumentation.
|  | Total fuel costs | EURO/MWh | 22.8543 | 22.8543 | 0% |  | 22.8543 | 22.8543 | 22.8543 | 22.8543 | See comment in this cell for more elaborate argumentation. | 22.8543 | 23.2074 | -1.522% |  | 23.2074 | 23.2074 |  | See comment in this cell for more elaborate argumentation.
Note on M13: Nick Rothengatter: The full load hours remain unchanged as the full load hours reported are too general to be of significant value. The load factor of fossil fuel plants such like a coal plant is often country specific.
Note on V13: Nick Rothengatter: The full load hours remain unchanged as the full load hours reported are too general to be of significant value. The load factor of fossil fuel plants such like a coal plant is often country specific.
Note on M18: Nick Rothengatter: For coal plants it is often assumed they have an technical lifetime of 40 years. The ETM follows the last OECD report of the IEA and NEA_2011 which indicates lifetime of 40 years. This figure is the most recent and most comparable for the Netherlands.
Note on M19: Nick Rothengatter: Most developers assume that dismantling costs will be compensated by the residual value of the power plant, and do not factor them into their calculation. We follow this method by setting both residual value as decommission costs equal to zero.
Note on V19: Nick Rothengatter: Most developers assume that dismantling costs will be compensated by the residual value of the power plant, and do not factor them into their calculation. We follow this method by setting both residual value as decommission costs equal to zero.
Note on C23: Nick Rothengatter: Is "all-in" or installed cost.s, which sums overnight construction costs and interst during construction (IDC).
Note on C24: Nick Rothengatter: IDC stands for interest during construction. The ETM doesn't use IDC but calculated the costs of capital. The cost of capital is the amount of money that is spent yearly to finance the required investment for the device. It assumes that the capital required either costs money to finance, or could have been used to generate money elsewhere. This is a percentage of the average investment over the lifetime of a device, which is called the WACC, the weighted average cost of capital. The WACC is very country specific. In the ETM the WACC is set to 6% for domestic appliances and to 10% for industrial and larger applications.
Note on C25: Nick Rothengatter: Analysts often refer to the construction costs as to “overnight cost” or undiscounted capital outlays. This is the cost that will be realized if the power plant could be built instantaneously or during one night. It does not incorporate financing charges and inflation during the construction time (IDC).
Note on C26: Nick Rothengatter: cost increases resulting from unforeseen technical or regulatory difficulties
Note on C27: Nick Rothengatter: EPC stands for Engineering, Procedurement and Construction. This is also known as the "Bare plant costs".
Note on C28: Nick Rothengatter: Owner's costs are the costs that are related to develop and start up the plant (e.g. land, cooling infrastructure, administration and associated buildings, site works, switchyards, project management, licences, etc.)
Note on M29: Nick Rothengatter: Most developers assume that dismantling costs will be compensated by the residual value of the power plant, and do not factor them into their calculation. We follow this method by setting both residual value as decommissioning costs equal to zero.
Note on V29: Nick Rothengatter: Most developers assume that dismantling costs will be compensated by the residual value of the power plant, and do not factor them into their calculation. We follow this method by setting both residual value as decommission costs equal to zero.
Note on J31: Nick: only variable cost are specified in the report
Note on M31: Nick Rothengatter: Calculated average. Deviation too big, therefore an expert from E.ON is consulted. Advice was to go for 20.00 EURO/MWe. This figure is supported by a study done by Harvard.
Note on V31: Nick Rothengatter: Calculated average. Deviation too big, therefore an expert from E.ON is consulted. Advice was to go for 20.00 EURO/MWe. This figure is supported by a study done by Harvard.
Note on M36: Nick Rothengatter: Calculated average. Deviation too big, therefore an expert from E.ON is consulted. The expert agreed to the current number.
Note on M47: Nick Rothengatter: For more information on how the ETM calculates CO2 costs a supplementary file can be given. If interested contact alexander.wirtz@quintel.com
Note on V47: Nick Rothengatter: For more information on how the ETM calculates CO2 costs a supplementary file can be given. If interested contact alexander.wirtz@quintel.com
Note on M48: Nick Rothengatter: For more information on how the ETM calculates fuel costs a supplementary file can be given. If interested contact alexander.wirtz@quintel.com
Note on V48: Nick Rothengatter: For more information on how the ETM calculates fuel costs a supplementary file can be given. If interested contact alexander.wirtz@quintel.com

## Output coal
Coal
|  |  | Coal pwd | New | Coal IGCC | New
| all costs excl tax and subsidies | sector | energy |  | energy
Technical
| Nominal electrical capacity | MW | 800 | 800 | 800 | 800
| Average effective output of nomimal capacity over lifetime | % | 99% | 99% | 98% | 98%
| full load hours | hour / year | 6950 | 6950 | 6324.11 | 6324.11
| electrical efficiency | % | 46% | 46% | 45.3% | 46%
| heat efficiency | % | 0 | 0 | 0 | 0
Cost
| Initial investment (excl CCS) | euro / MWe | 1250000 | 1499705.375 | 1650000 | 1928094.05
| Inititial investment per unit for CCS | euro / MWe | 0 | 0 | 0 | 0
| Cost of installing | euro / MWe | 0 | 0 | 0 | 0
| Residual value after lifetime | euro / MWe | 0 | 0 | 0 | 5
| Decommissioning costs | euro / MWe | 0 | 0 | 0 | 0
| fixed operation and maintenance costs | euro / MWe / year | 7679.1513 | 20000 | 21233.2483 | 20000
| variable operation and maintenance costs (excl CCS) | euro / full load hour | 2350 | 1382.4996 | 3800 | 801.248
| additional operation and maintenance costs for CCS (per full load hour) | euro / full load hour | 0 | 0 | 0 | 0
| Weighted average cost of capital | % | 0.1 | 0.1 | 0.1 | 0.1
| Do emissions have to be paid for through the ETS? | yes=1 / no=0 | 1 | 1 | 1 | 1
Other
| Land use per unit | km2 | 0.3 | 0.3 | 0.3 | 0.3
| Construction time | year | 3.5 | 3.5 | 5 | 5
| Technical lifetime | year | 30 | 40 | 30 | 30

## Supporting variables
Name | Value | Remarks
Exchange_rate_iea_2010 | 0.71585 | All costs were in 2008 USD
Exchange rate CEC_2009 | 0.695 | USD to EUR on 4 jan 2010
Exchange rate OECD_IEA_2010 | 0.74074
Exchange rate IEA_NEA_2010 | 0.68
Exchange rate DECC | 1.1
kw to MW | 1000
MW to GW | 0.001
GJ_to_MWh | 0.27778
Full capacity | 100%
pwd_capacity | 800
igcc_capacity | 800
# hours in a year | 8760
kilo to tonne | 1000
Full load hours_pwd_ETM_2008 | 6329.1
Full load hours_pwd_ccs_ETM_2008 | 5971.7106

## Reading guide
Reading guide
The excel file is set up to provide you an insight into the research done on the electricity generation costs that supports parts of the ETM input database. The excel file is built up by the following tabs:
1. Overview
The overview tab. Here you can find introducing remarks and coding explanation. Next to this the tab gives the outcomes and the changes of the total generation costs.
2. Assumptions
This tab gives you a list of the most important assumptions. More general assumptions about the ETM can be found on the wiki, her you can also find more information about the cost calculations: http://wiki.quintel.com/index.php/Documentation#Modeling_logic
3. Sources
Here you can find an alphabetically-sorted list of all the sources consulted. Sources can be used for multiple reasons (e.g. for lines of argumentation, definitions, costs data). Some of the consulted sources are used in the calculations tab, but most aren’t. A short reason why some sources are included but others aren’t can be found in the column next to the name of the source. The sources can be retrieved using the refmanager of the ETM: http://refman.et-model.com/
4. Notes
Each of the consulted sources contained information. What was judged as valuable information is noted here. As described above the information varies from definitions and general opinions or trends to more specific costs specifications.
5. Calculations
The so-called “heart” of the analysis. Whenever there were sources which outlined costs specifications these can be found back in the calculations tab. More detailed information about each of these values can be traced back to the notes page in which you can see from which report and page number these can be accessed to. Just use Ctrl+F in the notes tab using the name of your source of interest located in the calculations. The last column of each technology contains valuable comments in which you can find more elaboration.
6. Output ‘technology’
New output is compared to the old output. Data is retrieved from the results of the calculations tab. This new output is used in the input database for the ETM.
7. Supporting variables
Some of the calculations done are performed using supporting variables like hours_a_year , MW_to kW or value conversions (all data is recalculated to 2010 EURO). In this way it is easier to understand each of the recalculations done.