## Overview
Technology category |  | Waste
Version |  |  | 1 | Summary
Author |  | NR |  | The parameters have been derived from the state-of-the-art HR Centrale of the Afval Energie Bedrijf (AEB) in Amsterdam. The HR centrale is since August 2009 fully operational and functioning again after problems with its turbine have been fixed.
Date | Version | Changes
2012-02-23 | 1
|  |  |  | Certainties | Uncertainties
|  |  |  | · Investment costs | · full load hours
Coding |  |  |  | · Operating costs | · fuel and CO2 costs
Example | Value extracted from one of the reports referred to in notes
Example | Calculation |  |  | Total generation costs calculation outcomes: Waste |  |  | New ETM | Old ETM | %∆
Example | (default) Value as set by the ETM on 23-11-2011 |  |  | Total electricity generation costs |  | EURO/MWh | 113.1967 | 79.3564 | 42.64%
|  |  |  | Total capital costs |  | EURO/MWh | 48.7224 | 41.8013 | 16.56%
Introducing remarks |  |  |  | Total depreciation costs |  | EURO/MWh | 42.3673 | 36.3489 | 16.56%
· In this file you can find the research done on the generating costs of Waste |  |  |  | Total operating costs |  | EURO/MWh | 22.107 | 1.2062 | 1733%
· This research will update the attributes of this technology (see output tab) which will be used for the ETM. |  |  |  | Fixed operating costs |  | EURO/MWh | 0 | 0 | 0%
· Made fully available and transparent with the goal to stimulate the debate which will hopefully lead to a |  |  |  | Variable operating costs |  | EURO/MWh | 22.107 | 1.2062 | 1733%
continuous improvement of the ETM. |  |  |  | Total CO2 costs |  | EURO/MWh | 0 | 0 | 0%
· This research has made possible with help of the consulted sources, the knowledge within Quintel Intelligence |  |  |  | Total fuel costs |  | EURO/MWh | 0 | 0 | 0%
and external validation
· The following excel tabs relay information in the following order:
Sources à Notes à Calculations à Output
· Supporting information is provided in the tabs: assumptions, supporting variables, reading guide
· For more information about the ETM and its cost calculations visit
http://wiki.quintel.com/index.php/Documentation

## Assumptions
List of assumptions used
Assumptions
All costs are in 2010 EURO excl tax and subsidies
In calculations when certain values were not found values as set by the ETM on 23-11-2011 were used as an assumption (these values are colored red).
More general assumptions about the ETM can be found on the wiki, here you can also find more information about the cost calculations: http://wiki.quintel.com/index.php/Documentation#Modeling_logic
Powerplant is constucted on undeveloped (e.g. greenfield) land.

## Sources
List of sources used for converter specifications
| Number | Source | Finished | Used in calculations? | Refman ID
| 1 | AEB_2012_Productblad elektriciteit | Yes | No
| 2 | http://www.afvalenergiebedrijf.nl/ | Yes | Yes | Use weblink
| 3 | AEB_200603_Meer waarde uit afval | Yes | Yes, valuable source. Up-to-date information. | 2006_AEB_ET.Elt.wa
| 4 | AEB_2010_Jaarverslag 2009 | Yes | Yes | 2010_AEB_EB.Elb
| 5 | http://www.nieuwsbrief.amsterdam.nl/AEB-Nieuws/2012/AEB_Nieuws_8_12-01-2012000000.html#Hoogrendement Centrale draait boven ontwerpnorm | Yes | No
| 6 | Gemeente Amsterdam_20110504_Jaarrekening 2010 | Yes | Yes | 2011_BE.Br

## Notes
Source | Page | Notes | Calculations etc
AEB_2012_Productblad elektriciteit
Hoe kan dat?
Wij zetten uw dagelijks afval om in energie. In elektriciteit in dit geval en voeden daarmee het Amsterdamse net zodat alle trams en metro’s vooruit kunnen. En wij verlichten de hele stad inclusief de Stopera, Carré en meer. Daar is natuurlijk continu veel elektriciteit voor nodig. Welnu: daarom beschikken wij over Dankzij ons. En u! 1 Afvalenergiecentrale en 1 Hoogrendement Centrale die beiden afval omzetten in duurzame energie. De Hoogrendement Centrale wordt algemeen beschouwd als de modernste ter wereld.
Is dat duurzame energie? Absoluut. De energie die wij onze klanten leveren is schone energie. Dat is een eis die wij ons zelf stellen en het is wat de markt vraagt. Maar wat ook telt: wij zijn efficiënt in het omzetten van afval in energie. Onze score daarin is 30% en stijgend. Dat is zelfs op dit moment heel goed wereldwijd gezien. Ons doel is 40% in 2020. Gaan wij halen.
http://www.afvalenergiebedrijf.nl/ |  | Energiecentrales Het Afval Energie Bedrijf zet jaarlijks zo'n 1,4 miljoen ton afval om in elektriciteit, warmte en nuttige bouwstoffen. AEB beschikt over twee afvalgestookte energiecentrales die samen jaarlijks 1 miljoen MWh aan stroom opwekken. De Afvalenergiecentrale met een capaciteit van 850.000 ton afval per jaar is sinds 1993 in bedrijf. Deze Centrale heeft een elektrisch rendement van 24%. De Hoogrendement Centrale (HR Centrale) die in 2007 is opgeleverd heeft een elektrisch rendement van 30% en verwerkt 530.000 ton afval per jaar. Beide Centrales produceren zowel elektriciteit als warmte.
Beide Centrales produceren zowel elektriciteit als warmte. HR Centrale Met de ingebruikname van de Hoogrendement Centrale heeft AEB het elektrisch rendement, dat is de hoeveelheid stroom per afvalzak, en de producten die we uit rookgassen halen, verder opgevoerd. Meer energie en producten uit uitval. Nog minder belasting voor het milieu. Geen enkele andere centrale ter wereld voldoet beter aan deze maatschappelijke behoefte dan de HR Centrale.
Door de innovatieve toepassing van een herverhitter wordt de stoom halverwege het proces uit de turbine gehaald om voor de tweede keer te worden verhit. Zo ontstaat een nog hogere druk en temperatuur waardoor een elektrisch rendement van 30% mogelijk is!
AEB produceert 1 miljoen MWh stroom, goed voor 1% van de energiebehoefte van Nederland.
AEB verwerkt jaarlijks ruim 1,4 miljoen ton stedelijk- en bedrijfsafval. Dat is circa 20 tot 25% van het totaalaanbod van brandbaar afval in Nederland. Dit betekent een dagelijkse toevoer van 4.400 ton afval, ongeveer een half miljoen vuilniszakken per dag. Daarnaast verwerken we 100.000 ton rioolslib, afkomstig van Waternet.
De temperatuur in de verbrandingsketels is 1.000 tot 1.200 graden Celsius.
AEB_200603_Meer waarde uit afval
| 5 | HR Centrale (ontwerp) 57 MW 420.000 MWh elektriciteit
|  |  | 57 | MW | Nominaal vermogen
11
| 35 | Kosten en financiering
Er wordt een reductie van de kostprijs per ton afval van 5% verwacht ten opzicht van de bestaande Centrale die op zichzelf al de laagste kostprijs van Nederland heeft. Dit wordt gerealiseerd door de hogebeschikbaarheid en het hoge energetisch rendement van de Centrale. Daar komt nog bij, dat de HR Centrale, in verband met het milieuvriendelijke en innoverende karakter, diverse stimuleringsbijdragen zal ontvangen.
|  | Investeringsbedrag In 2003 heeft de Gemeenteraad van Amsterdam voor de bouw van de HR Centrale een bouwkrediet afgegeven van € 370 miljoen. Dit bedrag is opgebouwd uit € 290 miljoen voor de Centrale zelf. De overige 80 miljoen is bestemd voor ontwerp en management, bijkomende kosten, onvoorziene posten en bouwrente. Een aanvullend krediet en een aantal subsidies brengen het totale budget op € 371 miljoen. | 290000000 | EURO | Investering
|  |  | 20 | jaar | Technische levensduur
De afschrijftermijn van de investering is bepaald op 15 jaar. De technische levensduur zal 20 jaar of meer bedragen. Deze verlenging kan een belangrijke extra bijdrage leveren aan het rendement van de investering.
|  | 2004 Begin bouw Besteksengineering overige percelen Detailengineering hoofdpercelen Aanbesteding overige percelen 2005 Begin apparatenbouw Civiele ruwbouw gereed Opstart rioolwaterzuiveringsinrichting, biogasmotoren in bedrijf 2006 Afronding apparatenbouw Inbedrijfstelling | 3 | jaar | bouw
|  | Generator aantal 1 generator vermogen maximaal 74 MWel/86,8MVA geleverd vermogen nominaal 66 Mwel | 66 | MW | Nominaal vermogen
AEB_2010_Jaarverslag 2009 |  | Jaarverslag 2007
In de actualisatie is uitgegaan van een energetisch rendement van ongeveer 29%. In werkelijkheid is dit rendement door de technische problemen in de opstartfase 24% geweest. (jaarverslag 2007)
Algemeen (jaarverslag 2008) Op 27 mei 2008 is besloten om de HR Centrale met terugwerkende kracht vanaf 1 januari 2008 weer terug te brengen in de projectfase. Voor 2008 is vervolgens een nul resultaat afgegeven om financiële ruimte te creëren ter financiering van de herstelwerkzaamheden. Een niet goed functionerende turbine leidde vervolgens tot een lager dan verwacht energieresultaat en hogere operationele kosten, waardoor de financiële ruimte voor herstelwerkzaamheden minimaal bleek. Een eind 2008 door de gemeente Amsterdam verleend rendabel krediet van € 30 miljoen gaat de ruimte bieden om de noodzakelijke herstelwerkzaamheden te uitvoeren. In onderstaande toelichting wordt 2008 vergeleken met de actualisatie aangezien 2007 geen volledig productiejaar was
Bedrijfslasten jaarverslag (2008) De bedrijfslasten zijn € 3,4 miljoen hoger dan de actualisatie. Dit komt met name door hogere kosten voor de verwerking van reststoffen als gevolg van het niet optimaal functioneren van de HR Centrale. Hierdoor zijn extra kosten gemaakt om hoeveelheden reststoffen door externen te laten vervoeren. Daarnaast zijn er nog extra kosten gemaakt voor personeel van derden en onderzoek en advies die niet waren geactualiseerd.
8
[6 empty] | 2007 | 2008 | 2009 | 2010
Productie afvalenergiecentrale
[5 empty] | Verwerkt afval (ton) | 932700 | 873971 | 888800
[5 empty] | Geleverde elektriciteit (MWh) | 539891 | 507900 | 512355
[5 empty] | Geleverde warmte (GJ) | 161907 | 202770 | 151270
Productie HR centrale
[5 empty] | Verwerkt afval (ton) | 202000 | 436976 | 458000
[5 empty] | Geleverde elektriciteit (MWh) | 150198 | 90079 | 245772
[5 empty] | Geleverde warmte (GJ) | 0 | 11031 | 142400
Totaal
[5 empty] | Verwerkt afval (ton) | 1134700 | 1310947 | 1346800
[5 empty] | Geleverde elektriciteit (MWh) | 690089 | 597979 | 758127 | 880000
[5 empty] | Geleverde warmte (GJ) | 161907 | 213801 | 293670
[5 empty] | Operationele lasten | 122296 | 115589 | 144348
9
| 12 | Energie
Elektriciteit
In 2009 is in totaal 758.127 MWh geleverd uit de verbranding van afval. De Afvalenergiecentrale heeft 512.355
MWh opgewekt uit afval en de Hoogrendementcentrale 245.772 MWh uit afval. De hoeveelheid duurzame stroom
opgewekt uit afval komt overeen met het elektriciteitverbruik van circa 210.000 Amsterdamse huishoudens*.
In 2009 hebben de biogasmotoren 22.209 uur stand-alone gedraaid. In de 4 biogasmotoren is 9,3 miljoen Nm3
biogas en 19.830 Nm3 aardgas verwerkt. Hiermee is 19.956 MWh elektriciteit opgewekt. Dit komt overeen met het
elektriciteitverbruik van circa 5.500 Amsterdamse huishoudens.
Warmte
In 2009 was de hoeveelheid totaal geleverde warmte uit afval 293.670 GJ. Dit is een toename van 37% ten
opzichte van het voorgaande jaar tengevolge van verhoogde levering aan Westpoort Warmte en levering van
warmte van de HR Centrale.
In 2009 is met de 4 biogasmotoren 78.512 GJ warmte opgewekt.
12
12
Jaarverslag 2009
De HR Centrale is in het najaar van 2009 uit de projectfase volledig bedrijfseconomisch en met succes in gebruik genomen. In 2009 is de bedrijfsvoering van de Afvalenergiecentrale verder verbeterd. Dit heeft geleid tot een hogere omzet tegen lagere productielasten
De Hoogrendement Centrale Op 1 augustus 2009 is de Hoogrendement Centrale bedrijfseconomisch in gebruik genomen. In het Verbeterprogramma HR Centrale is naar dat moment toegewerkt. De verbeteringen hebben sindsdien geleid tot het succesvol realiseren van de ontwerpnormen van de HR Centrale. De gemiddelde gerealiseerde maandrendementen liggen op of boven de 30%. In 2009 is in de HR Centrale 458.000 ton afval verwerkt en er is 269.000 MWh elektriciteit opgewekt.
Operationele lasten De som van de operationele lasten over het boekjaar 2009 bedraagt € 144,3 miljoen en is daarmee € 28,8 miljoen hoger dan 2008 en € 0,9 miljoen lager dan in de actualisatie opgenomen. Het verschil met 2008 wordt met name veroorzaakt door het in gebruik nemen van de HR Centrale op 1 augustus 2009 waardoor vanaf dat tijdstip huur verschuldigd is (€ 15 miljoen per kwartaal). De andere belangrijke oorzaak voor het verschil is de activiteiten voor het 'Verbeterprogramma HR Centrale', die met € 12 miljoen verantwoord zijn onder de onderhoudslasten.
25
http://www.nieuwsbrief.amsterdam.nl/AEB-Nieuws/2012/AEB_Nieuws_8_12-01-2012000000.html#Hoogrendement Centrale draait boven ontwerpnorm |  | Hoogrendement Centrale draait boven ontwerpnorm Het Afval Energie Bedrijf is voortdurend bezig om te onderzoeken op welke wijze er nog meer energie en waardevolle materialen uit afval gehaald kunnen worden. Zo wordt ook onderzocht hoe we een maximaal rendement uit onze Hoogrendement Centrale (HR Centrale) kunnen halen. De inspanningen om de HR Centrale te optimaliseren hebben daarbij geleid tot een resultaat dat wereldwijd uniek te noemen is. De HR Centrale, in 2007 in gebruik genomen, is ontwikkeld om een elektrisch rendement van minstens 30 procent te behalen. In het afgelopen jaar is dat ook steeds ruimschoots gehaald, het jaargemiddelde was zo’n 31,4%. De centrale heeft zelfs uitschieters naar boven gerealiseerd van ruim 34%. AEB levert daarmee een nog grotere bijdrage aan de klimaatdoelstellingen van de gemeente Amsterdam.
|  |  | 0.314 | % | Efficiency
Gemeente Amsterdam_20110504_Jaarrekening 2010 | 217 | HRC
De exploitatie 2010 voor de Hoogrendement Centrale (HR Centrale) sluit met een positief saldo van € 5,8
|  | miljoen. De onderhoudslasten bestaan uit € 7,8 miljoen reguliere kosten en € 7,9 miljoen extra investeringen. | 7800000 | euro | Total O&M
Daarnaast is zoals gemeld bij de Begroting 2011, bij de actualisatie 2010, een dotatie gedaan aan de
voorziening groot onderhoud. Deze dotatie komt naar aanleiding van het meerjarenonderhoudsplan, dat
eind 2010 gereed kwam, uit op € 4,5 miljoen, waar in de geactualiseerde begroting voorlopig uitgegaan was
van een dotatie van € 3 miljoen. De dotatie voor 2010 heeft AEB in de Jaarrekening 2010 op basis van een
doorgerekende meerjarige onderhoudsplanning op € 4,5 miljoen gezet. In de Begroting 2010 is uitgegaan
van een resultaat van € 6,6 miljoen en in de geactualiseerde begroting van € 5,8 miljoen
Note on K121: Nick Rothengatter: uit 2010 jaarrrekening gemeente Amsterdam

## Calculations
Checks and balances and other calculations
Waste incinerator
Sources
|  |  | Data | New ETM | Old ETM | %∆ | %SD | AEB | Comments
Units/Region
Technical specifications
Capacity/yield
|  | Production capacity Gross | MWe | 57 | 55.5556 |  |  | 57 | Nominal capacity AEB
|  | Average effective output of nomimal capacity over lifetime | % | 97% | 97% |  |  | 97% | Assumed to be 97%, as standard in the ETM
|  | Production capacity Effective | MWe | 55.29 | 53.8889 |  |  | 55.29 | Calculation from gross capacity
|  | Net Electrical yield / efficiency | % | 31.4% | 25% |  |  | 31.4% | AEB 2011 yearly average
|  | Capacity factor/ Load factor | % | 70.66% | 70.66% |  |  | 70.66% | Calculation from full load hours
|  | Equivalent full load hours | hours | 6190 | 6190 |  |  | 6190 | Assumed to be 6190, as standard in the ETM
Other
|  | Construction time | years | 3 | 3 |  |  | 3 | Construction time AEB (2004 - 2006)
|  | Weighted average cost of capital (WACC) | % | 10% | 10% |  |  | 10% | Assumed to be 10%, as standard WACC in ETM for big power plants
|  | Technical lifetime | years | 20 | 20 |  |  | 20 | Estimated technical lifetime AEB
|  | Land use per unit | km2 | 0.5 | 0.5 |  |  |  | Assumed to be 0.5km2, as standard in the ETM
|  | Residual value | EURO/MW | 0 | 0 |  |  | 0 | See comment in this cell for more elaborate argumentation.
Finacial specifications
Investment costs
|  | Initial investment costs | EURO/MWe | 5245071.4415 | 4500000 |  |  | 5245071.4415 | Overnight costs of AEB excluding contingency, owner's and IDC costs.
|  | Construction cost | EURO/Mwe
|  | IDC | EURO/Mwe
|  | Overnight cost | EURO/Mwe
|  | Contingency costs | EURO/MWe
|  | Bare plant cost (EPC) | EURO/MWe
|  | Owner's costs | EURO/MWe
|  | Decommissioning costs | EURO/MWh | 0 | 0 |  |  | 0 | See comment in this cell for more elaborate argumentation.
Operating costs
|  | Fixed operating and maintenance costs | EURO/MWe/year | 0 | 0 |  |  | 0
|  | Personnel costs | EURO/MWe/year
|  | Insurance costs | EURO/MWe/year
|  | Connection costs | EURO/MWe/year
|  | Other | EURO/MWe/year
|  | Variable operating and maintenance costs | EURO/MWh | 22.107 | 1.2062 |  |  | 22.107 | AEB 2010 combined fixed and variable operating costs
|  | Consumables | EURO/MWh
|  | Raw fuel | EURO/MWh
|  | Other | EURO/MWh
Total generation costs calculation outcomes
|  | Total electricity generation costs | EURO/MWh | 113.1967 | 79.3564 | 42.64% |  | 113.1967
|  | Total capital costs | EURO/MWh | 48.7224 | 41.8013 | 16.56% |  | 48.7224
|  | Total depreciation costs | EURO/MWh | 42.3673 | 36.3489 | 16.56% |  | 42.3673
|  | Total operating costs | EURO/MWh | 22.107 | 1.2062 | 1733% |  | 22.107
|  | Fixed operating costs | EURO/MWh | 0 | 0 | 0% |  | 0
|  | Variable operating costs | EURO/MWh | 22.107 | 1.2062 | 1733% |  | 22.107
|  | Total CO2 costs | EURO/MWh | 0 | 0 | 0% |  | 0 | See comment in this cell for more elaborate argumentation.
|  | Total fuel costs | EURO/MWh | 0 | 0 | 0% |  | 0 | See comment in this cell for more elaborate argumentation.
Note on J19: Nick Rothengatter: Most developers assume that dismantling costs will be compensated by the residual value of the power plant, and do not factor them into their calculation. We follow this method by setting both residual value as decommission costs equal to zero.
Note on C23: Nick Rothengatter: Is "all-in" or installed cost.s, which sums overnight construction costs and interst during construction (IDC).
Note on C24: Nick Rothengatter: IDC stands for interest during construction. The ETM doesn't use IDC but calculated the costs of capital. The cost of capital is the amount of money that is spent yearly to finance the required investment for the device. It assumes that the capital required either costs money to finance, or could have been used to generate money elsewhere. This is a percentage of the average investment over the lifetime of a device, which is called the WACC, the weighted average cost of capital. The WACC is very country specific. In the ETM the WACC is set to 6% for domestic appliances and to 10% for industrial and larger applications.
Note on C25: Nick Rothengatter: Analysts often refer to the construction costs as to “overnight cost” or undiscounted capital outlays. This is the cost that will be realized if the power plant could be built instantaneously or during one night. It does not incorporate financing charges and inflation during the construction time (IDC).
Note on C26: Nick Rothengatter: cost increases resulting from unforeseen technical or regulatory difficulties
Note on C27: Nick Rothengatter: EPC stands for Engineering, Procedurement and Construction. This is also known as the "Bare plant costs".
Note on C28: Nick Rothengatter: Owner's costs are the costs that are related to develop and start up the plant (e.g. land, cooling infrastructure, administration and associated buildings, site works, switchyards, project management, licences, etc.)
Note on J29: Nick Rothengatter: Most developers assume that dismantling costs will be compensated by the residual value of the power plant, and do not factor them into their calculation. We follow this method by setting both residual value as decommission costs equal to zero.
Note on J47: Nick Rothengatter: For more information on how the ETM calculates CO2 costs a supplementary file can be given. If interested contact alexander.wirtz@quintel.com
Note on J48: Nick Rothengatter: For more information on how the ETM calculates fuel costs a supplementary file can be given. If interested contact alexander.wirtz@quintel.com

## Output Waste
The (new) output values are used to update the costs converters in the Energy Transition Model.
Waste
Incinerator
| all costs excl tax and subsidies | sector | old ETM | New ETM
Technical
| Nominal electrical capacity | MW | 55.56
| Average effective output of nomimal capacity over lifetime | % | 97%
| full load hours | hours/ year | 4078
| electrical efficiency | % | 28.6%
| heat efficiency | % | 0%
Cost
| Initial investment (excl CCS) | euro/MWe | 4500000
| Inititial investment per unit for CCS | euro/MWe | 0
| Cost of installing | euro/MWe | 0
| Residual value after lifetime | euro/MWe | 0
| Decommissioning costs | euro/MWe | 0
| fixed operation and maintenance costs | euro/MWe/year | 0
| variable operation and maintenance costs (excl CCS) | euro/ full_load_hour | 65
| additional operation and maintenance costs for CCS (per full load hour) | euro/ full_load_hour | 0
| Weighted average cost of capital | % | 0.1
| Do emissions have to be paid for through the ETS? | yes=1/no=0 | 1
Other
| Land use per unit | km2 | 0.5
| Construction time | years | 3
| Technical lifetime | years | 20

## Supporting variables
Supporting variables
Name | Value | Remarks
kw to MW | 0.001
# hours in a year | 8760
GJ_to_MWh | 0.27778
MW to GW | 0.001
GJ_to_MW | 1000

## Reading guide
Reading guide
The excel file is set up to provide you an insight into the research done on the electricity generation costs that supports parts of the ETM input database. The excel file is built up by the following tabs:
1. Overview
The overview tab. Here you can find introducing remarks and coding explanation. Next to this the tab gives the outcomes and the changes of the total generation costs.
2. Assumptions
This tab gives you a list of the most important assumptions. More general assumptions about the ETM can be found on the wiki, her you can also find more information about the cost calculations: http://wiki.quintel.com/index.php/Documentation#Modeling_logic
3. Sources
Here you can find an alphabetically-sorted list of all the sources consulted. Sources can be used for multiple reasons (e.g. for lines of argumentation, definitions, costs data). Some of the consulted sources are used in the calculations tab, but most aren’t. A short reason why some sources are included but others aren’t can be found in the column next to the name of the source. The sources can be retrieved using the refmanager of the ETM: http://refman.et-model.com/
4. Notes
Each of the consulted sources contained information. What was judged as valuable information is noted here. As described above the information varies from definitions and general opinions or trends to more specific costs specifications.
5. Calculations
The so-called “heart” of the analysis. Whenever there were sources which outlined costs specifications these can be found back in the calculations tab. More detailed information about each of these values can be traced back to the notes page in which you can see from which report and page number these can be accessed to. Just use Ctrl+F in the notes tab using the name of your source of interest located in the calculations. The last column of each technology contains valuable comments in which you can find more elaboration.
6. Output ‘technology’
New output is compared to the old output. Data is retrieved from the results of the calculations tab. This new output is used in the input database for the ETM.
7. Supporting variables
Some of the calculations done are performed using supporting variables like hours_a_year , MW_to kW or value conversions (all data is recalculated to 2010 EURO). In this way it is easier to understand each of the recalculations done.